## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2018 Examinations

Programme: Electrical Engg.

Subject: Testing & Maint. of Electrical Equip.(5104)/Testing & Maint. of

Electrical Machines(EE613) [Old/Rev]

# Time Duration: 3 Hrs.                                               Max. Marks: 75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | State the advantages and disadvantages of Regenerative testing. |  |
| b) | What is the necessity of polarity test on a transformer? Explain the polarity test briefly. |  |
| c) | Explain phasing out test for 3 phase transformer. |  |
| d) | List the methods of measurement of temperature rise in transformer winding. |  |
| e) | What are the various losses that take place in 3-phase induction motor? |  |
| f) | List and explain various losses in a synchronous machine. |  |
| g) | State the important points to be considered regarding care of electrical equipment during period of inactivity. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With a neat diagram, explain the brake test performed on a dc machine. |  |
| b) | With a neat circuit diagram, explain the Swinburne’s test on a d.c machine. How efficiency of d.c. machine is calculated from it? |  |
| c) | State the various losses occurring in d.c. machines as per IS classification. State parameters on which each depends. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | A 10KVA, 200/400V, 50Hz, 1 transformer gave following results: O.C. test 200V 1.3A 120W S.C. test 22V 30A 200W Find the parameters of equivalent circuit as referred to the primary i.e. LV winding. Draw suitable equivalent circuit. |  |
| b) | With a neat diagram, explain ratio test on a 1 transformer. State its significance. |  |
| c) | Explain the measuring of insulation resistance. How is it measured for power transformers? |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | State and explain the methods of temperature rise of various parts of induction motor. |  |
| b) | The input power to a 500V, 4-pole, 3 induction motor running at 1400 rpm is 40KW. The stator losses are 2KW and friction & windage losses are 1KW. Calculate i) Slip ii) Rotor copper losses iii) Efficiency. |  |
| c) | With a neat diagram explain HV testing of an induction motor. |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Compare direct and indirect method of testing electrical machines. -2- | ……2/- |
| b) | Write a note on computation of efficiency of synchronous machine from losses as per IS4389-1968. |  |
| c) | State and explain the acceptance tests to be performed on induction motor. Why these tests are necessary? |  |
| Q.No.6. | Write short notes on any two: | 2 x 6 = 12 |
| a) | Maintenance schedule on power transformer |  |
| b) | Pre-commissioning test on 3-phase induction motor |  |
| c) | Revarnishing process of winding of electrical equipment |  |

***********