## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

April, 2015 Examinations

Programme: Electrical Engg.

Subject: Testing & Maintenance of Electrical Equipments(5104)

# Time Duration: 3 Hrs.                                           Max. Marks: 75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | What do you mean by ‘regenerative testing’? State its advantages and disadvantages. |  |
| b) | For a d.c machine as a motor and as a generator, define i) Mechanical efficiency ii) Electrical efficiency & iii) Overall efficiency. |  |
| c) | Give the classification of losses taking place in d.c. machine as per I.S. |  |
| d) | How ratio test is performed on a three-phase transformer? What is the significance of this test? |  |
| e) | How do you separate hysteresis and eddy current losses in a transformer by calculation method? |  |
| f) | What should be minimum insulation resistance between all winding together and frame of an Induction motor rated as 100KW, 3.3KV, 3 Phase, 50Hz, 750rpm. Give rating of megger to be used. |  |
| g) | Why is the ‘sudden three phase short circuit test’ performed on synchronous machine? |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | - Justify the statement. Generally large capacity machines are tested by indirect method of testing - State the difference between type tests and routine tests. | (3) (3) |
| b) | A 500V, 20KW, 750rpm, field current 1.2A, d.c shunt generator is subjected to Swinburn’s test and following data are obtained: i) No load current at rated voltage = 3.7A ii) No load field current = 0.8A iii) Armature resistance = 0.2 ohm.Estimate the various losses and efficiency as per I.S. |  |
| c) | With a neat diagram explain the experimental setup and method for determination of efficiency of a D.C machine by using Brake test. What are its advantages and disadvantages? |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | What are the two high voltage tests to be performed on transformer? Give the frequency of high voltage and duration of application & waveshape of two impulses to which the power transformer is subjected to. |  |
| b) | Explain the meaning of insulation resistance. How is it measured for power transformer? What will you do if the value of insulation resistance between all windings to ground is 40 Kilo-ohms |  |
| c) | Enlist the various type tests to be performed on a transformer. | …….2/- |
|  | -2- |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | State and explain the methods of measurement of temperature rise of various parts of induction motor. |  |
| b) | A 415V, 3 phase, 6 pole, 0.8 p.f. star connected Induction motor has following data: No load input power = 250W No load current = 3.5A Stator resistance per phase = 1.5 ohm Full load current = 9.6 A Input power = 6000W Slip = 4% Find the efficiency of the motor by the summation of losses method. |  |
| c) | State and explain the acceptance tests to be performed on Induction motor. Why these tests are necessary? |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Enlist at least six tests to be performed on a synchronous Alternator to ensure safety and quality in operation. |  |
| b) | Describe the High voltage test for polyphase induction motor. |  |
| c) | What are the various methods of revarnishing of machine. Explain any one in detail. |  |
| Q.No.6. | Write short notes on any two: | 2 x 6 = 12 |
| a) | Causes of failure and trouble shooting of induction motor |  |
| b) | Maintenance schedule for power transformer |  |
| c) | Pre-commissioning tests on a 3-phase induction motor |  |

***********