## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

November, 2014 Examinations

Programme: Electrical Engg.

Subject: Testing & Maintenance of Electrical Equipments(5104)

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | What is meant by Type test, Routine test and Acceptance test? |  |
| b) | The per phase winding resistance measured at 30ºC for H.V. are found to be 1.3, 1.3 and 1.2 ohm. Give two possible causes and their effect on performance of transformer. |  |
| c) | What is the significance of ‘Polarity test’ to be performed on transformer? How this test is performed? |  |
| d) | Enlist the various methods of measurement of temperature rise of transformer winding? |  |
| e) | State the various type tests to be performed on a three phase induction motor. |  |
| f) | State the procedural steps for checking the three phase induction motor, if it fails to start. |  |
| g) | An alternator, rated 33KV, 1 MVA, 50Hz, 3000 rpm is subjected to insulation resistance test of duration 60 seconds & 10 seconds. Which of the two value will be lower and what is the minimum acceptable value of insulation resistance? |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | In a brake test, the effective load on the pulley was 37Kg, the effective diameter of the pulley 60 cms and speed 1440 rpm. The motor took 49A at 220V. Calculate the horse power and the efficiency of the motor. |  |
| b) | Draw the neat circuit diagram and explain the procedure for testing a d.c. machine by regenerative method of testing. |  |
| c) | Explain the various losses that are taking place in d.c. machines. What are the factors on which they depend? |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | With the help of a neat circuit diagram, describe the procedures for determining efficiency of transformer by Sumpner’s method. State two advantages and one main disadvantage. |  |
| b) | State the purpose of conducting high voltage tests on power transformers. Explain the tests in brief. Which tests are types tests and routine tests? |  |
| c) | Obtain the equivalent circuit of 200/400V 50Hz, 1-phase transformer from the following data: O.C. test:- 200V, 0.7A, 70W- on LV side S.C. test :- 15V, 10A, 85W on HV side. Calculate the secondary voltage when delivering 5 KW at 0.8 p.f. lagging. The primary voltage being 200V. |  |
|  |  | ……2/- |
|  | -2- |  |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain with a neat diagram open circuit voltage ratio test on a slip-ring induction motor. What is the significance of this test? |  |
| b) | The input power to a 500V, 4-pole, 3-phase induction motor running at 1400 rpm is 40KW. The stator losses are 2KW and windage & friction losses are 1 KW. Calculate i) slip ii) Rotor copper losses and iii) efficiency. |  |
| c) | Describe how the efficiency of a 3-phase induction motor can be calculated from the data obtained in No load and blocked rotor tests. |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Compare indirect and regeneration method of testing electrical machines. |  |
| b) | What is the object of carrying out the temperature rise test on three phase induction motor? How is it carried out? |  |
| c) | State the significance and explain the procedure of following tests on synchronous machine: i) Open circuit test ii) D.C. resistance of field winding and armature winding. |  |
| Q.No.6. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Furnish a recommended maintenance schedule for induction motors. |  |
| b) | Write a short notes on causes of failure of transformer and remedial measure. |  |
| c) | Explain the procedure of inspection of an electrical machine prior to its installation. |  |

***********